## Slide 1: IoT-Enabled Distributed SCADA & Machine Learning-Based Predictive Anomaly Detection for Multi-Process Industrial Systems
Developed By
Eklavya Vaid (B117), B.Tech (CE)
Arka Dhamani (A103), B.Tech (IT)
Krishna Solanki (I075), MBA Tech (IT)
Under the Guidance of
Dr. Dattatray Sawant
Sem : V Subject : SCADA
B Tech CE / IT | MBA Tech (IT)
Academic Year : 2026 - 2027
Notes: Introduce the team and the project: a four-layer SCADA testbed with an ESP32 edge node, LabVIEW supervision, a Python intelligence layer and a web digital twin.

## Slide 2: Aim & Objectives
Aim
Build a low-cost SCADA testbed that keeps a multi-hazard process safe with deterministic interlocks and adds machine learning that spots developing faults before they cause a trip.
1
Edge node
ESP32 reads 6 sensors, drives 3 actuators, serves Modbus TCP with fail-safe interlocks
2
Supervision
LabVIEW polls the node and exchanges JSON with the Python bridge
3
Intelligence
Advisory ML: anomalies, fault class, pump health, gas calibration, forecasts
4
Visibility
Web HMI with a 3D digital twin, alerts and a detection log
Notes: Aim: catch developing faults before they cause a trip, while keeping safety rule-based. Walk through the four objectives, one per layer.

## Slide 3: Four-Layer System Architecture
Layer 1 · ESP32 edge node
Level, temperature, gas, current, ambient, supply voltage · pump, valve, fan · local interlocks · Modbus TCP server
Layer 2 · LabVIEW SCADA
Modbus master, scaling, alarms, operator HMI, HTTP JSON client
Layer 3 · Python bridge
Validation, rule-based safety, ML engine, alerts and logs
Layer 4 · Web HMI & digital twin
3D workbench, live predictions, alert pop-ups, detection log
Modbus TCP
REST / WebSocket
Safety stays rule-based: the same thresholds run on the ESP32 and in the bridge. ML only raises alerts and advice, never switches an actuator.
Notes: Data flows ESP32 -> LabVIEW (Modbus TCP) -> Python bridge (HTTP JSON) -> web HMI. Commands flow back down. Safety is enforced in the ESP32 and the bridge; ML is advisory.

## Slide 4: Components used in Hardware
ESP32 DevKit V1
HC-SR04 level
DS18B20 temp
MQ-2 gas
ACS712 current
BME280 ambient
0-25 V sensor
Relay module
Submersible pump
Solenoid valve
40 mm fan
16x2 I2C LCD
Breadboards
Notes: Thirteen parts make up the as-built rig. Sensors on the top rows, actuators and HMI below. The pump is a 12 V / 5 V mini centrifugal pump (about 0.1-0.5 A).

## Slide 5: Hardware Connections: ESP32 Pin Map
GPIO | Connected to
34 | HC-SR04 ECHO (1k/1.5k divider)
25 | HC-SR04 TRIG
4 | DS18B20 data (4.7 kΩ pull-up)
32 | MQ-2 AO (divider)
33 | ACS712 OUT
35 | 0-25 V sensor S
21 / 22 | I2C: LCD + BME280
GPIO | Connected to
26 | Pump relay IN
27 | Drain valve driver
14 | Exhaust fan driver
23 | Green LED (healthy)
13 | Red LED (alarm)
2, 12, 15 | Kept free (boot pins)
TX0 / RX0 | Kept free (USB flashing)
Power: 5 V 2 A rail for logic, sensors, relay and LCD; separate 12 V 2-3 A rail for pump, valve and fan; common ground. ESP32 3.3 V feeds the BME280 and DS18B20. Flyback diodes on the valve and fan coils.
Notes: Boot-strapping pins 2, 12 and 15 are left free; the LEDs were moved to 23 and 13 for that reason. All 5 V signals into the ESP32 go through dividers.

## Slide 6: Hardware Setup & Integration Status
[TO ADD] Insert photo of the assembled hardware rig
Integration checklist
✓
Power rails, 12 V barrel jack
✓
HC-SR04, MQ-2, BME280
✓
ACS712, voltage sensor
✓
Pump relay, LCD, status LEDs
DS18B20 4.7 kΩ pull-up
Valve + fan driver wiring
MQ-2 R0, tank depth, divider ratios
Wi-Fi credentials, node IP
Notes: Most wiring is verified. Remaining: DS18B20 pull-up, valve and fan driver wiring, and the calibration constants in the firmware. Replace the box with a photo of the assembled rig.

## Slide 7: ESP32 Firmware & Fail-Safe Interlocks
Condition | Action | LED
Tank ≥ 88 %, gas ≥ 250 ppm, temp ≥ 70 °C or current ≥ 3.8 A | Master trip: pump off, drain opens on overflow | Red strobe
Sensor faulty or MQ-2 warming up | Fail-safe: pump off, fan on while gas unknown | Red solid
Gas > 80 ppm | Exhaust fan on (off below 45 ppm) | —
Tank ≤ 25 %, all sensors healthy | Auto refill: pump on, valve closed | Green
Real conversions
ACS712 (V - V0)/185 mV/A with boot zero; MQ-2 LPG curve
Non-blocking
DS18B20 converts in the background so Modbus stays responsive
Builds
Board + Wokwi targets · 14.9 % RAM · 81.7 % flash
Notes: The firmware trips on hard limits and also fails safe on any sensor fault: a dead sensor writes 0x7FFF so the bridge can never mistake it for a real reading.

## Slide 8: Modbus TCP Register Map
Address | Signal | Scaling
40001 | Tank level | ÷10 → %
40002 | Process temperature (signed) | ÷10 → °C
40003 | Gas concentration | ppm
40004 | Pump current | ÷100 → A
40005 | Ambient temperature (signed) | ÷10 → °C
40006 | Relative humidity | ÷10 → %RH
40007 | Pressure | ÷10 → hPa
40008 | Supply voltage | ÷100 → V
40009 | MQ-2 raw output | mV
00001-3 | Pump / valve / fan coils | Boolean
0x7FFF
Fault sentinel
Written instead of a reading when a sensor is faulty, missing or warming up. It is out of range for signed and unsigned reads, so the bridge rejects it and inhibits the pump.
Notes: LabVIEW reads 9 holding registers and 3 coils from port 502, unit 1. Registers 40002 and 40005 are signed. 32767 means the sensor is faulty or warming up.

## Slide 9: VI’s used in Front Panel
1
JKI Flat UI Controls
Flat gauges, indicators and switches
2
Waveform charts
Live trends of level, temperature, gas, current
3
Boolean indicators
Alarm lamps and actuator states
4
String indicator
Bridge recommendation and ML advisory
[TO ADD] Insert screenshot of the LabVIEW front panel
Notes: Show the front panel: tank, temperature, gas and current indicators, alarm lamps and actuator switches. Replace the box with a screenshot of SCADA_Master_Controller.vi.

## Slide 10: VI’s used in Block Diagram
1
NI Modbus Library
TCP master: read 9 registers + 3 coils, write coils
2
Scaling & alarm logic
Engineering units, signed reads for 40002/40005
3
Flatten / Unflatten JSON
Telemetry cluster ↔ JSON packet
4
HTTP Client POST
Sends telemetry, receives actuator commands
[TO ADD] Insert screenshot of the LabVIEW block diagram
Notes: Walk through one polling cycle: open Modbus session, read registers and coils, scale, build the JSON packet, POST to the bridge, parse the reply and write the actuator coils.

## Slide 11: Python Bridge: From Telemetry to Alerts
Validate
Reject bad or out-of-range data
Safety rules
HEALTHY / WARNING / TRIP + interlocks
ML engine
5 advisory models
Debounce
Raise after 4, clear after 8
Alert & log
HMI pop-up, events.csv
Endpoint | Purpose
POST /api/telemetry | LabVIEW packet in, health + actuator commands out
GET /api/predictions | Live ML predictions, alerts, model status
GET /api/alerts | Active alerts and detection history
POST /api/control | Operator command, subject to interlocks
Notes: Every packet goes through the same pipeline. Invalid data trips to UNKNOWN immediately. Alerts need 4 consecutive detections to raise and 8 clean samples to clear.

## Slide 12: Predictive Analytics: Five Models
1
Anomaly detection
Mode envelope + Isolation Forest
Is something off?
2
Fault classification
Random Forest, 24-sample window
Which of 9 faults is it?
3
Pump health
Gradient Boosting regressor
How worn is the pump (0-100)?
4
MQ-2 calibration
Gradient Boosting + datasheet
True ppm at this temperature and humidity?
5
Forecasting
Linear trend over ~60 samples
When will a limit be reached?
Notes: Each model answers one operator question. None of them can switch an actuator. Gas compensation and forecasts work even before any training.

## Slide 13: Why Two Anomaly Detectors
Chart: Faults flagged (%), sim profile
| Dry run | Blockage | Overload | Tank leak | Stuck relay | Overheat
Mode envelope | 95.6 | 63.9 | 99.9 | 99.9 | 100 | 40.5
Isolation Forest | 0 | 0 | 0.1 | 0 | 0.4 | 4.7
1.6%
false alarms per sample before debouncing
Envelope catches out-of-range dynamics; the forest is a second opinion on odd combinations of in-range readings.
Notes: Isolation Forest alone missed nearly every fault: its splits stop at the edge of the training data, so readings far outside it are not isolated faster. The mode envelope measures distance from normal and catches them.

## Slide 14: Machine Learning Results
96.0%
fault classifier accuracy (sim)
34% → 6%
MQ-2 error with T/RH compensation
0
false alerts in a 60 s normal live run
Chart: Fault classifier recall per class (%)
| Normal | Gas leak | Overheat | Dry run | Blockage | Overload | Tank leak | Stuck relay | Valve stuck
Sim (96.0%) | 98 | 98 | 77 | 97 | 94 | 99 | 91 | 99 | 97
Rig (96.3%) | 99 | 98 | 98 | 94 | 91 | 63 | 96 | 98 | 92
Notes: Evaluated on held-out simulated episodes with a different seed. Overall fault accuracy is about 96 % on both profiles; the weakest classes are overheating (sim) and motor overload (rig).

## Slide 15: Digital Twin & Web HMI
3D workbench: CAD models, wiring check, firmware model, fault injection
[TO ADD] Insert screenshot of the Predict panel during a fault
Notes: The 3D workbench mirrors the rig, validates wiring and runs the firmware model with fault injection. The Predict panel shows live predictions; alerts pop up from any view.

## Slide 16: Testing & Validation
Completed
Backend tests 15 / 15, frontend tests 15 / 15
Firmware builds for board and Wokwi
Live feeder run: dry run, gas leak, stuck relay, overload, worn pump all detected
Normal run: zero false alerts
On the rig (pending)
Test | Result
Level vs ruler (±1 cm) | [TO ADD]
DS18B20 vs thermometer | [TO ADD]
ACS712 vs multimeter | [TO ADD]
LabVIEW 200 ms poll | [TO ADD]
Overflow / gas trip | [TO ADD]
Sensor-fault fail-safe | [TO ADD]
Alarm latency < 1 s | [TO ADD]
Notes: Software and simulation testing is complete. Hardware validation is planned; fill in measured values after final wiring.

## Slide 17: Conclusion & Future Scope
Conclusion
Complete four-layer SCADA stack, firmware to web HMI
Rule-based safety on ESP32 and bridge
ML catches faults that never cross a threshold
Remaining: final wiring, calibration, on-rig tests
Future scope
Retrain models on logged rig data
Calibrate MQ-2 against a reference meter
Scale to three nodes (gas/fire, electrical load)
Secure Modbus / VPN and HMI login
Time-series historian and trend views
Notes: Close with what was delivered, what remains (final wiring, calibration, on-rig retraining) and where it can go next.

## Slide 18: THANK YOU
Questions & Discussion
Notes: Invite questions.