## Slide 1
PROJECT PROPOSAL
IoT-Enabled Distributed SCADA & Machine Learning Diagnostics
Design Proposal for a Four-Layer Distributed Process Control & Safety System
DEVELOPED BY
Eklavya Vaid (B117) — B.Tech CE
Arka Dhamani (A103) — B.Tech IT
Krishna Solanki (I075) — MBA Tech IT
PROJECT PARAMETERS
Guided by: Dr. Dattatray Sawant
Semester V | Subject: SCADA
Academic Year 2026–2027

## Slide 2
SCADA PROJECT PROPOSAL
Project Vision & Objectives
01
Distributed Edge Control
• Deploy cheap, localized ESP32 microcontrollers as RTUs rather than a single expensive DAQ.
• Utilize Wi-Fi networking to allow independent, localized loops that avoid central wiring hazards.
• Ensure local node safety: nodes default to safe outputs if network connectivity is lost.
02
Supervisory Orchestration
• Leverage LabVIEW as the central SCADA hub to orchestrate distributed processes.
• Run closed-loop PID control and safety interlocks (Emergency Shutdown Matrix) at a deterministic 200ms rate.
• Package live plant tags into JSON payloads for external diagnostic ingestion.
03
Intelligent Operations
• Establish a local Python backend (FastAPI) to process telemetry and host WebSockets.
• Deploy Machine Learning (Random Forest classifier) to predict sensor drift and system faults before they trigger ESD.
• Serve a high-fidelity React dashboard for modern operator monitoring and manual overrides.
02

## Slide 3
SCADA PROJECT PROPOSAL
Proposed 4-Layer SCADA Architecture
1
Physical Edge Nodes (ESP32) | Protocol: Modbus TCP/IP (Port 502)
3 independent wireless nodes running Arduino C++ server code. Acquire level, temperature, gas, and grid load telemetry locally and execute local safety loops.
2
Supervisory SCADA Engine (LabVIEW) | Protocol: Modbus Client & HTTP Client
Central control loop polls edge nodes every 200ms. Runs closed-loop PID level/heating control, evaluates safety interlocks, and pushes JSON telemetry to the API.
3
Intelligence Backend (Python FastAPI) | Protocol: REST API & WebSockets
Receives JSON telemetry logs, runs real-time Machine Learning classification ( anomaly detection ), logs data, and broadcasts data + status predictions via WebSockets.
4
Operator Web HMI (React) | Protocol: WebSocket Client Connection
High-fidelity, responsive single-page browser dashboard (Vite + Tailwind). Renders live trend charts (Recharts), gauge alarms, and allows remote manual overrides.
03

## Slide 4
SCADA PROJECT PROPOSAL
Layer 1: Proposed Wireless Edge Nodes
NODE 1: PROCESS PLANT
Static IP: 192.168.1.101
PROPOSED SENSORS:
• HC-SR04 Ultrasonic (Liquid Level)
• DS18B20 1-Wire (Temperature)
PROPOSED ACTUATORS:
• 5V Relay for Submersible Pump
• 12V Ceramic Heating Cartridge
NODE CONTROL LOGIC:
Simulates a liquid control chamber. LabVIEW reads level & temp, running closed-loop PID control outputs back to the node to actuate the pump & heater.
NODE 2: SAFETY & HAZARDS
Static IP: 192.168.1.102
PROPOSED SENSORS:
• MQ-2 Gas / Smoke Sensor
• Infrared Flame/Fire Sensor
PROPOSED ACTUATORS:
• 5V Active Piezo Buzzer (Alarm)
• 5V DC Brushless Exhaust Fan
NODE CONTROL LOGIC:
Monitors environmental hazards. Highest priority node. If thresholds are breached, local interrupts sound the buzzer and trip the LabVIEW safety shutdown.
NODE 3: POWER SUB-STATION
Static IP: 192.168.1.103
PROPOSED SENSORS:
• ACS712 Current Sensor (5A)
• Voltage Divider Circuit (0-25V DC)
PROPOSED ACTUATORS:
• 5V Dual-Channel Relay (Breakers)
• 12V DC Auxiliary Test Loads
NODE CONTROL LOGIC:
Simulates an electrical grid breaker. Measures load current and voltage. LabVIEW monitors power metrics and executes load-shedding if overload is detected.
04

## Slide 5
SCADA PROJECT PROPOSAL
Components Used in Hardware
MICROCONTROLLERS & SENSORS
• ESP32 NodeMCU Development Board — 3 Qty
• HC-SR04 Ultrasonic Distance Sensor — 1 Qty
• DS18B20 Waterproof Temperature Sensor — 1 Qty
• MQ-2 Combustible Gas Sensor Module — 1 Qty
• Infrared Flame / Fire Sensor Module — 1 Qty
• ACS712 Current Sensor Board (5A) — 1 Qty
• Voltage Sensor Module (0-25V DC Divider) — 1 Qty
ACTUATORS & UTILITIES
• 5V Submersible Water Pump + Tubing — 1 Qty
• 12V Ceramic Heating Cartridge — 1 Qty
• 5V DC Brushless Fan (Exhaust Vent) — 1 Qty
• 5V Single-Channel Relay Modules — 2 Qty
• 5V Dual-Channel Relay Board — 1 Qty
• Active Piezo Buzzer Board — 1 Qty
• 12V DC Auxiliary Load Bulbs/Motors — 2 Qty
• Wi-Fi Router (Local Gateway Node) — 1 Qty
• Breadboard & Interconnecting Jumper Wires — 1 Set
05

## Slide 6
SCADA PROJECT PROPOSAL
Proposed Modbus Register Mapping
All ESP32 wireless nodes will run standard Modbus TCP servers on Port 502, mapped with the following register addresses:
Node | Register Type | Address | Parameter / Tag Name | Scale & Format
Node 1 (192.168.1.101) | Input Register | 30100 | Water Level Percentage | 0 - 100% (Integer)
Node 1 (192.168.1.101) | Input Register | 30101 | Liquid Temperature | Temp * 10 (Float scale)
Node 1 (192.168.1.101) | Coil | 00200 | Water Pump Status | 0 = Off, 1 = On
Node 1 (192.168.1.101) | Holding Register | 40300 | Heater Power Level | 0 - 100% (Duty cycle)
Node 2 (192.168.1.102) | Input Register | 30100 | Combustible Gas Levels | PPM concentration
Node 2 (192.168.1.102) | Discrete Input | 10200 | Infrared Flame Detection | 0 = Safe, 1 = Fire Detected
Node 2 (192.168.1.102) | Coil | 00300 | Ventilation Fan Control | 0 = Off, 1 = On
Node 3 (192.168.1.103) | Input Register | 30100 | Substation Load Current | Current draw in mA
Node 3 (192.168.1.103) | Input Register | 30101 | Grid Bus Voltage | Voltage level in mV
Node 3 (192.168.1.103) | Coil | 00200 | Relay Breakers 1 & 2 | 0 = Open, 1 = Closed
06

## Slide 7
SCADA PROJECT PROPOSAL
Layer 2: LabVIEW Supervisory Engine (Proposed)
PROPOSED CONTROL LOOPS
• Deterministic Polling: Set up a LabVIEW Producer-Consumer loop mapping to the 3 Modbus TCP IPs, polling registers every 200ms.
• Hysteresis Level Control: Run a simple level bang-bang hysteresis band loop in LabVIEW. If level < 40%, water pump turns ON. If level > 80%, pump turns OFF to prevent pump wear.
• Temperature PID Loop: Deploy standard LabVIEW PID.vi targeting a setpoint. Output value (0-100) will be clamped and written to Node 1's holding register, modulating heater PWM.
PROPOSED SAFETY INTERLOCKS (ESD)
• Continuous Safety Checks: Implement a logic matrix in LabVIEW evaluated before committing any outputs. Safety interrupts override normal control outputs instantly.
• Emergency Shutdown (ESD): If Node 2 registers high gas PPM or fires the flame sensor, LabVIEW will force immediate shutdown state: pump OFF, heater 0%, buzzer ON, exhaust fan ON, load relays OPEN.
• Modbus Loss Watchdog: If LabVIEW misses Modbus telemetry connection for >3 consecutive cycles (600ms), it automatically trips the local plant to prevent unmonitored hazards.
07

## Slide 8
SCADA PROJECT PROPOSAL
VI's Used in Front Panel
• JKI FLAT UI CONTROLS PACK
Package Link: https://vipm.io/package/jki_flat_ui_controls/ | Replaces standard gray controls with modern flat buttons, indicators, switches, and graphs.
• LABVIEW WEBSOCKETS LIBRARY (MEDIAMONGRELS)
Package Link: https://vipm.io/package/mediamongrels_lib_websockets/ | Allows browser HMI client to connect and capture telemetry data stream directly.
• JKI JSON SERIALIZATION LIBRARY
Package Link: https://vipm.io/package/jki_lib_json_serialization/ | Converts cluster UI controls to web-readable JSON variables for UI updates.
• JKI HTTP REST CLIENT
Package Link: https://vipm.io/package/jki_lib_rest_client/ | Allows UI trigger events to execute POST requests to Python endpoints.
• MQTT LIBRARY FOR LABVIEW
Package Link: https://vipm.io/package/ni_lib_mqtt/ | Enables visual indicator tags to subscribe directly to cloud messaging brokers.
08

## Slide 9
SCADA PROJECT PROPOSAL
VI's Used in Block Diagram
• NI MODBUS LIBRARY
Package Link: https://vipm.io/package/ni_lib_modbus/ | Instantiates Modbus Master TCP sessions to connect, poll, and write to the 3 ESP32 nodes.
• NI PID CONTROL TOOLKIT VIS
Package Link: https://www.ni.com/en-support/downloads/toolsnetwork/pid-control-toolkit.html | Calculates closed-loop thermal response outputs using PID.vi on Node 1.
• LABVIEW DATABASE CONNECTIVITY TOOLKIT
Package Link: https://www.ni.com/en-support/downloads/software-products/download.database-connectivity-toolkit.html | Enables logging telemetry strings directly to local databases (Access/SQL/CSV).
• LABVIEW HTTP CLIENT (HTTP CLIENT.LVLIB)
Package Link: https://www.ni.com/en-support/downloads/software-products/download.labview.html | Built-in POST engine executing JSON transmissions to FastAPI server endpoints.
• LABVIEW JSON SERIALIZATION (JSON.LVLIB)
Package Link: https://www.ni.com/en-support/downloads/software-products/download.labview.html | Built-in palette VIs used to flatten clusters to raw JSON strings on the diagram.
09

## Slide 10
SCADA PROJECT PROPOSAL
Layer 3: Python Backend & ML (Proposed)
PROPOSED FASTAPI API SURFACE
• REST /api/telemetry (POST): Receives the raw JSON data packets from LabVIEW's HTTP Client every 200ms.
• WebSocket /ws/live: Broadcasts the incoming telemetry and active ML classifications to all connected React web clients.
• Historian Logger: Appends telemetry logs to a local database (CSV or SQLite) to build a historical time-series model.
• REST /api/history (GET): Exposes API endpoint for React frontend to backfill historical trend charts when loading.
PROPOSED MACHINE LEARNING MODEL
• Feature Input Vector: Reads four parameters: [Level %, Temperature °C, Gas PPM, Current draw mA] in real-time.
• Training Strategy: We will write a python script to generate a synthetic training dataset simulating healthy cycles, sensor drift, leak anomalies, and electrical grid spikes.
• Random Forest Classifier: We will train a Random Forest classifier in Python, export it as a .pkl file, and load it into FastAPI to classify state in under 5ms.
• Operational Classes: Output health diagnostics: Class 0 (Healthy), Class 1 (Warning: Sensor Drift/Low Current), Class 2 (System Anomaly/Fault - triggers alarm).
10

## Slide 11
SCADA PROJECT PROPOSAL
Layer 4: React Web HMI Dashboard (Proposed)
PROPOSED WEB DASHBOARD STACK
• React & Vite: Build a lightweight Single Page Application (SPA) leveraging Vite for compilation and rendering speed.
• Tailwind CSS: Apply rich, responsive dark-mode styling with glassmorphic cards (semi-transparent backgrounds with borders) matching modern automation interfaces.
• Low-Latency WebSockets: Connect the web browser directly to the FastAPI server. Renders live sensor fluctuations with sub-100ms latency.
PROPOSED VISUAL COMPONENTS
• Real-time Charts: Integrate Recharts libraries to plot sliding line graphs tracking water level and temperature fluctuations over time.
• Color-Coded Status Gauges: Implement radial gauge charts for gas PPM. Add visual indicators showing water pump, exhaust fan, and circuit breaker status.
• ML Diagnostic Panel: Show a diagnostic console displaying the active ML health classification, prediction probability, and time since the last update.
11

## Slide 12
SCADA PROJECT PROPOSAL
Proposed Implementation Timeline
PHASE 1 (Weeks 1–3)
Hardware & Polling
• Procure all sensors & ESP32s
• Implement Modbus TCP code
• Verify local sensor accuracy
• Establish LabVIEW polling loop
PHASE 2 (Weeks 4–6)
Backend API & ML
• Construct FastAPI server
• Develop JSON ingestion endpoint
• Collect training data records
• Train Random Forest model
PHASE 3 (Weeks 7–8)
React Dashboard
• Structure React frontend
• Establish WebSockets link
• Plot real-time telemetry
• Implement override commands
PHASE 4 (Weeks 9–10)
Integration & Test
• Integrate all four layers
• Validate safety ESD interlocks
• Calibrate current thresholds
• Final project presentation
12

## Slide 13
SCADA PROJECT PROPOSAL
Expected Deliverables & Outcomes
PROPOSED HARDWARE & SOFTWARE DELIVERABLES
• Functional Hardware Testbed: Three wireless nodes successfully executing sensor acquisition and relay controls over Modbus TCP.
• LabVIEW SCADA Core: A local program that aggregates node telemetry, handles PID control, safety overrides, and logs telemetry values.
• Python FastAPI Server: Hosts REST interfaces and broadcasts streams with low latency.
• React HMI Operator Dashboard: A browser-based SPA showing live gauges, switches, and trend lines.
EXPECTED OPERATIONAL CRITERIA
• Polling Loop Success: Maintain a stable 200ms supervisory cycle time in LabVIEW with zero dropped Modbus frames under normal operations.
• Low-Latency Alarm Response: If a gas leak or fire is detected, system trips to ESD state and annunciates on the React web HMI in under 1 second.
• ML Diagnostic Accuracy: Train the anomaly classifier to achieve >90% validation accuracy on the simulated dataset.
• Local Watchdog Functionality: Verify that if Wi-Fi connection drops, nodes instantly isolate their relays locally to prevent unmonitored operation.
13

## Slide 14
THANK YOU
Questions & Discussion